Questions Log – AAH1802 webinar “CMS Conditions of Participation”

Q: Are windows required in Observation? What about in NICU?

A: Buildings must have an outside window or outside door in every sleeping room, and for any building constructed after July 5, 2016 the sill height must not exceed 36 inches above the floor. Windows in atrium walls are considered outside windows for the purposes of this requirement.

(i) The sill height requirement does not apply to newborn nurseries and rooms intended for occupancy for less than 24 hours.

(ii) The sill height in special nursing care areas of new occupancies must not exceed 60 inches.

Q: Out of curiosity, why do we go to cornell.edu for information regarding the conditions of participation in lieu of the CMS website?

A: The cornell.edu website is one of the easier websites to navigate for the information. You could also go directly to the federal register for the information.

Q: Can you elaborate on the 36" sill height, is that a maximum dimension or something else?

A: The 36” sill height is a maximum sill height.

Q: What is a CMS k-tag?

A: K-Tags are the survey citations that CMS uses in their survey system. They align with specific section of the codes and standards adopted by CMS. They are used as a survey tool, to help guide survey teams through a systematic approach to the survey, they may not represent the all of the codes and standards section that may be cited. Each provider type has its own survey report, the hospital report can be found here: https://www.cms.gov/Medicare/CMS-Forms/CMS-Forms/downloads/cms2786R.pdf

Q: Requirements for ALFs?

A: CMS does not have a reimbursement program for Assisted Living Programs therefore there are no conditions or participation. States may have licensing requirements for Assisted Living Facilities.

Q: Explain about one or more for AHC. The IBC calls one or more but rules don't apply until four.

A: Both the IBC and NFPA codes take a somewhat scalable approach to ambulatory care. In the IBC, one person rendered incapable results in the facility being classified as an ambulatory care facility. It’s still a Group B (business) occupancy class, and the special requirements in Section 422 are triggered when you cross certain size thresholds. NFPA classifies all facilities with four or more as an ambulatory Healthcare Occupancy. Similar to the IBC the base requirements are identical to the Business occupancy, and additional requirements kick in as the facility gets larger.

CMS complicates this somewhat by changing the occupancy threshold in NFPA from four to one.

Q: I have heard there may be a new CMS requirement that physical separation between a Cancer Center Clinic and Infusion Center. Separation meaning they can no share support space, waiting room etc. Are you aware or have information on this?

A: We are not aware of this specific interpretation, it may relate to certain licensure rules in the state.  Generally speaking, surveyors often look to see clear boundaries between portions of the building that participate in different licensing programs or different reimbursements programs. Always ask for a code section and citation to understand the source of the requirement.

Q: CMS reviewer is asking New Jersey State hospital to modify pre-existing ICU's with "borrowed light" rooms to comply with FGI rules for window. Building was built in 1970's and these rooms were "grandfathered". Why is CMS coming in now and mandating this compliance?

A: CMS does not adopt the FGI Guidelines, however the state typically does. In many instances, the CMS reviewer is also the reviewer that verifies compliance with state hospital licensing rules. In some cases, you would want to verify the state rules and most importantly the adopting language. Often, previous conditions are “grandfathered” in if you can verify that it complied with the regulations at the time it was constructed. There are a few conditions that states may have determined create a hazard and require retroactive upgrades.

Q: I understand that when only one patient is not able to evacuate by himself, CMS requires that this facility that needs to receive reimbursement to comply with NFPA 101 and 99. Can you please give us example of these surgery center types? Is dental surgery included? Why plastic surgery is not included?

A: The conditions of participation specifically remove the flexibility in the Life Safety Code to utilize a “lesser” occupancy for facilities that serve 3 or fewer patients that are incapable of self-preservation.   Dental and Plastic surgery may be included if they are participating in Medicare/Medicaid program, however the majority of the dental and plastic surgeries don’t qualify for reimbursement (e.g. elective surgeries) therefore many do not have to meet the Conditions of Participation.

Again, facilities are not required to participate in the Medicare/Medicaid program – but if they choose to, they must follow the rules.

Q: Under CMS, do Ambulatory Surgery Centers and Ambulatory Health Centers (no surgical service) follow the same Part?

A: Distinct Entity (stand alone, not under a hospital leadership) Ambulatory surgery centers that are participating in Medicare/Medicaid services (meaning that they will be accepting Medicare/Medicaid patients) must meet Part 416. Ambulatory Health Centers without surgical services, may or may not be providing covered services for Medicare/Medicaid services, therefore would not need to comply with the conditions of participation (and the Life Safety Code as adopted by CMS)

Q: Would an ambulatory surgical center still qualify as distinct if it contains other clinical floors focusing on outpatient services?

A: An ASC satisfies the criterion of being a “distinct” entity when it is wholly separate and clearly distinguishable from any other healthcare facility or office-based physician practice. The ASC is not required to be housed in a separate building from other healthcare facilities or physician practices, but, in accordance with National Fire Protection Association (NFPA) Life Safety Code requirements (incorporated by cross reference at §416.44(b)), it must be separated from other facilities or operations within the same building by walls with at least a one-hour separation. If there are State licensure requirements for more permanent separations, the ASC must comply with the more stringent requirement.

Q: Is there a written interpretation for the 1 hour rated separation at ambulatory surgical center waiting areas?

A: https://www.cms.gov/Medicare/Provider-Enrollment-and-Certification/SurveyCertificationGenInfo/downloads/SCLetter10_20.pdf

Q: Is the CMS Survey checklist available on line?

A: https://www.cms.gov/Medicare/CMS-Forms/CMS-Forms/downloads/cms2786R.pdf

Q: Any COP requirements governing inpatients using an outpatient space, i.e. outpatient radiology suite?

A: We are not aware of the current guidance on CMS for this issue.

Q: Has CMS issued a clarification for the anti-ligature requirements for non-psychiatric hospitals?

A: Not yet. The most recent S&C letter from November 2017 stated that they anticipated a six-month process

Q: What is the best way for us as designers to keep up with S&C's since there are a lot issued and very few impact physical environment?

A: The American Society for Healthcare Engineering monitors and alerts members to new S&C letters that impact physical environment. They maintain a list, short description of topics and other compliance materials with the memos. http://www.ashe.org/resources/member/physcms.shtml

Q: Is there a place where we can find the interpretation letters from CMS?

A: The American Society for Healthcare Engineering monitors and alerts members to new S&C letters that impact physical environment. They maintain a list, short description of topics and other compliance materials with the memos. http://www.ashe.org/resources/member/physcms.shtml

Q: Daylight requirement in NICU?

A: Buildings must have an outside window or outside door in every sleeping room, and for any building constructed after July 5, 2016 the sill height must not exceed 36 inches above the floor. Windows in atrium walls are considered outside windows for the purposes of this requirement.

(i)	The sill height requirement does not apply to newborn nurseries and rooms intended for occupancy for less than 24 hours.

Note that your state may have licensing rules that relate to this topic.

Q: I am curious as to why CMS does not simply adopt FGI so we would have more universal regulations to follow?

A: The Conditions of Participation only cover Life Safety Requirements.

Q: Do you enforce the 5# opening force on windows in patient rooms and if so what kind of windows have you seen that have met the ADA requirements?

A: The Americans with Disabilities Act is a separate statue. To my knowledge the conditions of participation do not alter any provisions of this Act. The question of scope and compliance depends upon what Title of the Act you fall under (generally Title II applies to governmental program and Title III applies to private entities). ADA operates a great technical assistance line at 1-800-514-0301.

Q: Which payer system is used for an outpatient service being used in an inpatient facility?

A: Hospital based outpatient services are common and are reimbursed through the Hospital Outpatient Prospective Payment.