## Slide 1: Academy of Architecture for Health On-line Professional Development
Building Enclosure Fundamentals—Air Barriers for Health Care Facilities
HC 101 Series
Tuesday, May 9, 2017
2:00 pm – 3:00 pm ET
1:00 pm – 2:00 pm CT
12:00 am – 1:00 pm MT
11:00 am – 12:00 pm PT
Presenter
Kevin Kalata, RA, SE
Wiss, Janney, Elstner & Associates
Moderator
John Kreidich
McCarthy Building Companies

## Slide 2
Health Care 101 Series
The Academy’s multi-channel on-line approach provides emerging professionals, journeymen, and master professionals with convenient and economical opportunities to develop their chosen area of interest.
The HC 101 Series sessions are tailored to provide budding healthcare design professionals with conceptual and practical primer-level knowledge.
Series topics include: Master planning; Programming; Ambulatory care; Clinical support services; Emergency; ICI-acute care; Imaging; Long-term care; Maternal care; Mental health; Surgery.

## Slide 3
Copyright Materials
This presentation is protected by US and International Copyright laws. Reproduction, distribution, display and use of the presentation without written permission of the speaker is prohibited.
©2017 The American Institute of Architects

## Slide 4
Compliance Statement
“AIA Knowledge” is a Registered Provider with The American Institute of Architects Continuing Education Systems (AIA/CES). Credit(s) earned on completion of this program will be reported to AIA/CES for AIA members. Certificates of Completion for both AIA members and non-AIA members are available upon special request.
This program is registered with AIA/CES for continuing professional education. As such, it does not include content that may be deemed or construed to be an approval or endorsement by the AIA of any material of construction or any method or manner of handling, using, distributing, or dealing in any material or product.

## Slide 5
AIA/CES Reporting Details
All attendees will be eligible to receive: 1 AIA LU/HSW (AIA continuing education)
In order to receive credit, each attendee must complete the webinar survey/report form at the conclusion of the presentation.
Follow the link provided:
in the Chat box at the conclusion of the live presentation;
in the follow-up email you (or the person who registered your site) will receive one hour after the webinar.

## Slide 6
Questions?
Submit a question to the moderator via the chat box.
Content-related questions will be answered during the Q&A portion at the end as time allows.
Tech support questions will be answered by AIA staff promptly.

## Slide 7
Building Enclosure Fundamentals—Air Barriers for Health Care Facilities
Presenter
Kevin Kalata, RA, SE
Wiss, Janney, Elstner Associates, Inc.
847-272-7400
kkalata@wje.com

## Slide 8
Outline
Building Science
  General Overview
Air Barriers
  Performance Requirements
  Types
  Testing Procedures
Additional Considerations for Enclosure Design
  Heat Flow
  Moisture

## Slide 9
Building Enclosure Fundamentals
Air Barriers for Health Care Facilities
Building Science

## Slide 10
Building Science Basics
Definition
Building science
Can be defined as the study of the movement of air, moisture, and energy through the building envelope

## Slide 11
Building Science Basics
Enclosure Problems
Insert leakage, air barrier, condensation issues, etc.

## Slide 12
Building Science Basics
Enclosure Problems

## Slide 13
Building Science Basics
Overview
Involved in all aspects of the building enclosure design
Principles relate to structures everywhere
Key to understanding moisture problems
Primary goals are to reduce energy costs & prevent moisture problems

## Slide 14
Building Science Basics
Overview
Air movement
  Air barriers
  Drying and moisture transport
Heat energy movement
  Insulation effect & placement
  Material conductivity
Moisture problems
  Water leakage
  Vapor diffusion

## Slide 15
Building Enclosure Fundamentals
Air Barriers for Health Care Facilities
Air Barriers

## Slide 16
Air Movement & Barriers
Air Flow Concepts
Air Movement
High to low pressure
Pressurization affected by:
  Wind effects
  Mechanical systems
  Stack effect
Transports: Heat & Vapor

## Slide 17
Air Movement & Barriers
Wind Pressurization
External Pressures
  Windward
  Leeward
Internal Pressures
  Positive and negative pressure
  Affected by: Building type (open, closed, partially enclosed)
External Pressures
Internal Pressures (per ASCE 7)
Enclosure Classification | (Gcpi)
Open Buildings | 0.00
Partially Enclosed Buildings | +/- 0.55
Enclosed Buildings | +/- 0.18
Windward
Pressure
Leeward
Pressure
WIND

## Slide 18
Air Movement & Barriers
Mechanical Pressurization
Exhaust
Negative Internal Pressure
Outside Air

## Slide 19
Air Movement & Barriers
Mechanical Pressurization
Positive Internal Pressure
Outside Air
Exhaust

## Slide 20
Air Movement & Barriers
Mechanical Pressurization
Return Air (Vent Restricts Airflow)
Fan
Vent
Supply
Return

## Slide 21
Air Movement & Barriers
Mechanical Pressurization
Stack Effect: Hot Climate
COOL
Stack Effect

## Slide 22
Air Movement & Barriers
Mechanical Pressurization
Stack Effect: Cold Climate
WARM
COLD
Stack Effect

## Slide 23
Air Movement & Barriers
Barrier Definition
Air Barrier
Materials assembled and joined together to provide a barrier to air leakage through the building envelope. An air barrier may be a single material or a combination of materials.
- 2015 IECC

## Slide 24
Air Movement & Barriers
Air Barrier Requirements
Continuous across thermal envelope
Joints & seams sealed. Penetrations caulked, gasketed, or sealed
Seals & detailing must resist positive and negative pressures
Penetrations must not affect integrity of air barrier (e.g., recessed light fixtures)

## Slide 25
Air Movement & Barriers
Air Barrier: Code Requirements
International Building Code
International Energy Conservation Code
ASHRAE 90.1 – Energy Standard for Buildings Except Low-Rise Residential Buildings

## Slide 26
Climate Zones
Air Movement & Barriers
Air Barrier: Code Requirements
2015 IECC
Figure C301.1

## Slide 27
Air Movement & Barriers
Code Requirements – Building Envelope
2000 – Leakage rates for fenestration & openings but no opaque criteria.
2006 – Envelope is to be sealed to limit air infiltration.
2012 – Continuous air barrier required throughout the building envelope (except Climate Zones 1, 2, and 3).
2015 - Continuous air barrier required throughout the building envelope (except Climate Zone 2B

## Slide 28
Air Movement & Barriers
Code Requirements – Opaque Envelope
Allowable air leakage at 0.3 in. w.g. (75 Pa)
Material: < 0.004 cfm/ft2 (0.02 L/s·m2)
Assembly: <0.04 cfm/ft2 (0.2 L/s·m2)
Building: <0.4 cfm/ft2 (2.0 L/s·m2)
Air Leakage Tests

## Slide 29
Air Movement & Barriers
Types
Air Barrier Options:
  Vapor permeable
  Vapor non-permeable
  Often serves as moisture barrier

## Slide 30
Air Movement & Barriers
Air Barrier Placement
Exterior of sheathing
Insulation in cavity
Sheet on interior of studs
Precast Concrete with Spray Foam

## Slide 31
Air Movement & Barriers
Air Barrier Types
Sheet goods
Liquid applied
Self adhering membranes
Spray foam insulation
Concrete
Others*
  Metal, Gypsum board, Extruded polystyrene, Foil-backed polyiso, etc.

## Slide 32
Air Movement & Barriers
Air Barrier Types
Sheet Good

## Slide 33
Air Movement & Barriers
Air Barrier Types
Liquid Applied

## Slide 34
Air Movement & Barriers
Air Barrier Types
Self Adhering Membrane

## Slide 35
Air Movement & Barriers
Air Barrier Types
Spray Foam Insulation

## Slide 36
Air Movement & Barriers
Air Barrier Types
Sealed Insulated Board

## Slide 37
Air Movement & Barriers
Air Barrier Detailing Considerations
Continuity of system
Interface detailing
  Roof/Wall, Fenestration, Floor lines, Shelf Angles, Soffits, Canopies, Base of Wall, Etc.
Movement considerations
Material compatibility

## Slide 38
Air Movement & Barriers
Air Barrier Detailing Considerations
Interface detailing
  Storefront Window System

## Slide 39
Air Movement & Barriers
Air Barrier Detailing Considerations
Interface detailing
  Storefront Window System
Jamb Condition

## Slide 40
Air Movement & Barriers
Air Barrier Detailing Considerations
Continuity / Interface detailing
Fenestration interface detailing

## Slide 41
Air Movement & Barriers
Air Barrier Detailing Considerations
As-built condition
Air barrier repair
Thermal barrier repair
Continuity / Interface detailing

## Slide 42
Air Movement & Barriers
Air Barrier Detailing Considerations
Interface detailing
  Curtain Wall

## Slide 43
Air Movement & Barriers
Air Barrier Detailing Considerations
Movement considerations
Deflection track
EIFS reveal
Sealant joint
Floorline Detail

## Slide 44
Air Movement & Barriers
Air Barrier Detailing Considerations
Movement considerations
Floorline detailing options
Membrane Transition
Preformed Silicone Transition
Expansion Joint
Membrane Flashing

## Slide 45
Air Movement & Barriers
Air Barrier Detailing Considerations
Continuity
Gap below angle
Exposed sheathing
Shelf angle detail

## Slide 46
Air Movement & Barriers
Air Barrier Detailing Considerations
Continuity at shelf angles
Air Breach in Humid Climate + Negative Pressurization = Interior Summertime Condensation

## Slide 47
Air Movement & Barriers
Air Barrier Detailing Considerations
Material compatibility
Sealant & Air Barrier Flashing
Interface
Most silicones will not bond to polyethylene

## Slide 48
Gaps/Voids
Unsealed penetrations
Extended exposure to UV light
Thin application
Temperature restrictions
Moisture restrictions
Air Movement & Barriers
Air Barrier Application Issues

## Slide 49
Air Movement & Barriers
Air Barrier: QA/QC Testing
Air Barrier Testing
Quantitative
  Air flow
  Adhesion
Qualitative
  Continuity
  Interface detailing

## Slide 50
Air Barriers
Quality Assurance / Quality Control
ASTM E783
Quantitative: Air Flow

## Slide 51
Air Barriers
Quality Assurance / Quality Control
ASTM D4541
Quantitative: Adhesion
Minimum Pull-Off Strength:16 psi

## Slide 52
Air Barriers
Quality Assurance / Quality Control
ASTM E1186
Qualitative: Continuity
Pressurization/Depressurization coupled with:
  Infrared
  Tracer Gas
  Liquid Surfactant
“Bubble Gun” Testing
Tracer Gas

## Slide 53
Air Barriers
Quality Assurance / Quality Control
Infrared Imaging
Anomalies may represent air breaches or presence of moisture
Critical factors for proper imaging
  High temperature gradient
  Angle of incidence
  Solar positioning

## Slide 54
Upcoming Break for Questions and Comments
Submit a question to the moderator via the chat box.

## Slide 55
Building Enclosure Fundamentals
Air Barriers for Health Care Facilities
Additional Considerations
Thermal, Moisture, & Vapor

## Slide 56
Additional Considerations
Thermal, Moisture, & Vapor
Heat Energy Movement
Conduction (heat flow through materials)
Convection (heat flow through air/fluid currents)
Radiation (Heat flow through space)

## Slide 57
Additional Considerations
Heat Energy Movement
Heat energy moves from hot to cold
Energy movement through the wall or roof system is reduced by insulation (thermal barrier)
  The higher the R-value, the higher the reduction in heat transfer
  Thermal bridges can greatly affect the insulation performance

## Slide 58
Additional Considerations
Heat Energy Movement: Typical R-Values
Insulation | R-value per inch
Fiberglass Batt | 3.1 to 3.4
Mineral Wool Batt | 3.1 to 3.4
Mineral Wool Board | 3.1 to 4.3
Expanded Polystyrene (EPS) | 3.8 to 4.6
Extruded Polystyrene (XPS) | 5.0
Polyisocyanurate | 5.6 to 8.0
Open Cell Spray Foam (SPF) | 3.5 to 3.6
Closed Cell Spray Foam (SPF) | 6 to 6.5

## Slide 59
Additional Considerations
Heat Energy Movement: Code Requirements

## Slide 60
Additional Considerations
Heat Energy Movement: Code Requirements
IECC Commercial Requirements: |  |  |  |  |  | 
Minimum R-Value for Metal Framed Walls |  |  |  |  |  | 
Climate Zone | 2000 | 2003 | 2006 | 2009 | 2012 | 2015
1 | R-0 | R-0 | R-13 | R-13 | R-13 + R-5ci | R-13 + R-5ci
2 | R-11 | R-11 | R-13 | R-13 | R-13 + R-5ci | R-13 + R-5ci
3 | R-11 | R-11 | R-13 | R-13 + R-3.8ci | R-13 + R-7.5ci | R-13 + R-7.5ci
4 | R-11 | R-11 | R-13 | R-13 + R-7.5ci | R-13 + R-7.5ci | R-13 + R-7.5ci
5 | R-11 | R-11 | R-13 + R-3.8ci | R-13 + R-7.5ci | R-13 + R-7.5ci | R-13 + R-7.5ci
6 | R-11 | R-11 | R-13 + R-3.8ci | R-13 + R-7.5ci | R-13 + R-7.5ci | R-13 + R-7.5ci
7 | R-13 | R-13 | R-13 + R-7.5ci | R-13 + R-7.5ci | R-13 + R-7.5ci | R-13 + R-7.5ci
8 | R-13 | R-13 | R-13 + R-7.5ci | R-13 + R-7.5ci | R-13 + R-7.5ci | R-13 + R-7.5ci
ci = continuous insulation
Metal Framed Wall Requirements

## Slide 61
Enclosure Design
Heat Energy Movement: Insulation Options
Insulation
in Stud Space
Hybrid System
Insulation
in Cavity

## Slide 62
Enclosure Design
Heat Energy Movement: Insulation Efficiency
ASHRAE 90.1 - Table A3.3
Only 35% effective
Stud Cavity Batt Insulation

## Slide 63
Additional Considerations
Heat Energy Movement: Affects of Insulation Placement
Exterior
0.0°F
Interior
70.0°F
39.7°F
]
13.7°F
]
57.4°F
]
39.6°F
]
61.6°F
]
55.9°F
]
67.0°F
]
57.9°F
]
68.4°F
]
64.9°F
]
67.4°F
]
66.4°F
]
Insulation in stud space
Hybrid
Continuous insulation
Exterior
0.0°F
Interior
70.0°F
Exterior
0.0°F
Interior
70.0°F

## Slide 64
Additional Considerations
Condensation
Condensation
Change in phase from vapor to a liquid. Surface condensation occurs when water vapor contacts a non-porous surface that has a temperature lower than the dew point of the surrounding air.
- ASHRAE Fundamentals
Dew Point
A measure of atmospheric moisture. The temperature to which the air must be cooled in order to reach saturation (assuming air pressure and moisture are constant).
- NOAA

## Slide 65
Additional Considerations
Condensation
Concrete Column with Steel Embed
Sweating on Back Side of Steel Studs

## Slide 66
Additional Considerations
Condensation
Factors Affecting Condensation
Temperature & Relative Humidity
Insulation Type & Placement
Thermal Bridging
Air Barrier Continuity
Building Pressurization
Vapor Retarder Placement / Type
Interior Layout / Barriers

## Slide 67
Laboratories
Healthcare Facilities
Natatoriums
Additional Considerations
Condensation: High RH Spaces & Negative Pressurization

## Slide 68
Moisture penetrates the envelope by:
  Water leakage
  Air infiltration
  Vapor diffusion
Additional Considerations
Moisture Sources

## Slide 69
A measure of a material or assembly’s ability to limit the amount of moisture that passes through that material or assembly
Class I: <= 0.1 perm
Plastic extrusion
Foil scrim kraft paper
Spray foam insulation*
Class II: > 0.1 perm <= 1.0
Class III: > 1.0 perm <=10 perm
Additional Considerations
Vapor Diffusion

## Slide 70
Very slow process (less than airflow)
Vapor retarders control diffusion
  Can be combined with air barrier and/or moisture barrier
  Should be located on the “warm” side of the wall
  Only one vapor retarder per wall assembly
Additional Considerations
Vapor Diffusion

## Slide 71
Common Vapor Retarders:
  Polyethylene film
  Fluid-applied vapor retarder
  Self-adhering sheet membranes
  Aluminum foil/FSK
  “Smart” vapor retarders
Other Materials that Serve as Vapor Retarders
  Oil and epoxy based paints
  Polystyrene board insulation (XPS)
  Vinyl wall coverings
  Sheet metal & glass
Additional Considerations
Vapor Diffusion

## Slide 72
Insulation
in Stud Space
Hybrid System
Insulation
in Cavity
“Cold” Climate
“Hot” or “Cold” Climate
Additional Considerations
Vapor Retarder Placement

## Slide 73
Warm/humid climate
“Smart” vapor retarder
Perforated vinyl wall covering
“The product is not suited for cooling climates with high outdoor humidities… Do not use with vinyl wall coverings or vapor retarding paints”
- Manufacturer’s Literature
Additional Considerations
Vapor Diffusion Issues: Hot Climate

## Slide 74
Condensation on sheathing
Vapor retarder on cold side of insulation
Additional Considerations
Vapor Diffusion Issues: Cold Climate

## Slide 75
Building Enclosure Fundamentals
Summary
Air barriers serve to reduce energy consumption and help mitigate moisture issues with the building envelope
Continuity, integration, and compatibility are key to air barrier design, installation, and performance
Performance of healthcare building enclosures are dependent on the performance of not only the air barrier, but also moisture barrier, thermal barrier, and vapor retarder
Thermal barrier code changes as well as interior design conditions make healthcare facilities especially susceptible to increased risk of condensation

## Slide 76
Time for Questions and Comments
Moderator
John Kreidich
McCarthy Building Cos.
???-!!!

## Slide 77
CES Credit
All attendees are eligible to receive: 1.0 HSW/CEU (AIA continuing education)
Attendees at your site can submit for credit by individually completing the webinar’s survey and report form. The survey closes Friday, May 12, 2017at 12:30 am EDT.
The URL to the webinar survey/form https://www.research.net/r/AAH1704 will be emailed to the person who registered your site.
More continuing education questions? Email . . . knowledgecommunities@aia.org.

## Slide 78
Join us at The Academy of Architecture for Health!
• Receive Academy Update newsletters
• Access to resources
  Knowledge Repository
  Webinars
  Award programs
  Scholarships, Fellowships
  Emerging professionals benefits
  National and regional conferences and events
  Social media, publications, blogs, and Twitter

## Slide 79
To join us or update your account go to . . .
www.aia.org/aah
Click here

## Slide 80
Upcoming Webinars*
Date | Series | Topic
6/13 | Design Award Case Study Series | Kaiser Permanente Kraemer Radiation Oncology Center
7/18 | Outside The Box Series | Architecture for Health
8/8 | Masters Studio Series | The Highly Reliable Hospital
*Dates and topics are subject to change
Visit www.aia.org/aah for more information and to register.